RRMX-1/RRMX-2 - Maximum Security GRILLE w/removable perforated face plate(s) 

Contractor shall furnish and install risk resistant grille model RRMX-1/RRMX-2 as herein specified or where shown on the plans. The units shall be as manufactured by Anemostat Products. The RRMX-1 and RRMX-2 shall be of all steel welded construction. The face plate will be of 12 GA steel (RRMX-1) with 5/32" on 7/32" perforated holes ( for risk resistance) with a 1/2" "hug tight" lip to accommodate a secondary 14 GA face plate mated and spot welded to the front face giving an overall 3/16" seamless face plate appearance (RRMX-2). An optional stainless steel (16-16-mesh) screen will be spot welded to the back of the face plate for further risk and contraband reduction. The face plate will be attached by pinned flat head torx security screws to a face flange of the sleeve. The locking angles will be shipped loose for field installation by others. Unit shall be finished with factory white powder coat.